## Slide 2: CPO – HP oil separation unit Oil separation in liquid R717
HP liquid containing oil
CPO variants/options:
Stand alone
Combined with receiver
With oil cooler liquid priority
Defrost hot gas supply
< 1 ppm oil
Advantages:
Oil stays on HP side, no pollution or breakdown
Very simple oil return system
Maintenance free oil management
No oil consumption
Disadvantage:
Increased refrigerant charge
Dry clean oil to compressors
HB- oil
switches
Separation: Require knowledge about oil not commonly available
Proof of concept:
ARLA Taulov Dairy, Denmark
173 liters of oil found in 23 weeks.
No oil found on LP side

## Slide 3: Oil management
120ppm
120ppm
35ppm
35ppm
>1ppm oil
Note !
High TC (heat pump) : De-gassing vessel necessary